Diagnose and repair A/C Condenser does not come on.

Proposal to:

troubleshooted bldg 358 outdoor liquid chiller, found open windings on both outdoor condenser fan motor, fan motors not operating, checked voltage to both condenser fan motors, both had correct voltage on all 3 legs. Removed 2 damaged motors from outside condenser, both condenser motors are OEM and has to be purchased from factory.

1 to 3 day lead time

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Diagnose and repair A/C Condenser |  |  |  |  |  |  |  |  |
| CSS #30846 - CMI #13333 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 06.14.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 150.00 | 8 |  |  |  |  |  | $ 1,200.00 |
| 1.2 2 HP York OEM Motors |  |  |  |  | $ - | $ - | $ - | $ 3,528.74 |
| 2 @ 1764.37 each 1 - 3 day lead |  |  |  |  |  |  |  |  |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 4,728.74 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 150.00 | 2 |  |  |  |  |  | $ 300.00 |
| 2.2 CE Factor 1.03% |  |  |  |  |  |  |  | $ 150.86 |
| Grand Total |  |  |  |  |  |  |  | $ 5,179.60 |