Repair screens around the chimney vents. Dead birds were found inside of the units during PM.

Tech found work while performing the Maintenance.

Proposal to:

Installing cap on top of main chimney located approx 60 to 80 feet in air to prevent starling birds from entering boiler located in mechanical room (pictures were sent) these birds completely blocked combustion to boiler causing boiler to malfunction and going off on intermittent safety controls.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Repair screens around the chimney vents |  |  |  |  |  |  |  |  |
| CSS #30857 - CMI #13335 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 05.28.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 16 |  |  |  |  |  | $ 1,600.00 |
| 1.2 Equipment Rental |  |  |  |  | $ - | $ - | $ - | $ 2,650.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 4,250.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE factor 1.03% |  |  |  |  |  |  |  | $ 127.50 |
| Grand Total |  |  |  |  |  |  |  | $ 4,377.50 |