Description of Repair:  Troubleshoot and Repair High Efficiency Triad Boilers, One in Building 356 and One in Building 208, F12 Code.

JOB DESCRIPTION

found both Triumph condensing type boiler not firing, along with Triad boiler going off on safety. Must replace low water cut off control board along with low water insertion type probes. Triad boiler needs electrode and sensor replaced. This will stop nuisance safety failures. Condensing Triumph boiler. Isolate and drain down boilers to replace low water cut off and sensing probe. Disconnect existing electronic control board and replace with new type revised control board. Must be rewired to accept new control board design. Triad boilers – must replace electrode and sensor probes. Disconnect from underneath power flame burner access panel. Pull electrode assembly out and replace with new.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Troubleshoot and Repair High Efficiency |  |  |  |  |  |  |  |  |
| CSS #33548 - CMI #15542 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 11.23.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 16 |  |  |  |  |  | $ 1,600.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 3,503.36 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 5,103.36 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor .90% |  |  |  |  |  |  |  | $ (510.34) |
| Grand Total |  |  |  |  |  |  |  | $ 4,593.02 |