** EMERGENCY CALL **

Need plumber to repair emergency pipe break today

Proposal to:

Emergency service call and repair heating system were completely down on building 208. Also, emergency repairs for bldg 356, pressure relief valve blowing off.

Bldg 208 found water pouring out of baseboard radiator located on first floor. Had to drain heating system located in mechanical room in sub-basement. Cut out damaged piping located in radiator and replaced with new shark bite couplings. Build system install radiator covers and filled system at boiler location.

Bldg 356 found pressure relief valve weak and blowing water out of boiler. Found damaged and defective pressure reducing valve which was allowing to much water to fill system. Installed new pressure relief valve and re-pipe to existing drain, install new B&G 25-pound capacity pressure reducing valve. Had to re-pipe to accept new valve.

** Work has already been completed, EMERGENCY Call **

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Need plumber to repair emergency |  |  |  |  |  |  |  |  |
| CSS #35433 - CMI #16880 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 04.22.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor BLDG 356 | $ 125.00 | 8 |  |  |  |  |  | $ 1,000.00 |
| 1.2 Labor BLDG 208 | $ 125.00 | 5 |  |  |  |  |  | $ 625.00 |
| 1.1 Material BLDG 356 |  |  |  |  | $ - | $ - | $ - | $ 320.00 |
| 1.2 Material BLDG 208 |  |  |  |  | $ - | $ - | $ - | $ 675.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,620.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.03% |  |  |  |  |  |  |  | $ 78.60 |
| Grand Total |  |  |  |  |  |  |  | $ 2,698.60 |