Follow up quote for repaired ruptured coil.

Initial: Repair roof ruptured heating coil at building #354. Coil must have frozen during power outage.

This proposal is for prevention of coils freezing and rupturing due to power failures when outside air dampers are open during cold outside temperatures causing stagnation of water in heating coil. There are provisions to install glycol to heating system this will require pumping in 50 gallons of glycol into main heating system located in mechanical room on lower level filling up both Triumph condensing boiler as well as vertical type Triad boiler, time will be spent draining entire heating system for all heating coils, pumping in 50 gallons of glycol into entire heating system, removing all air out of entire system to put system back into safe operation. This work should be performed when heating system is no longer needed either before cooling season or before heating system starts.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Follow up quote for repaired ruptured coil |  |  |  |  |  |  |  |  |
| CSS #91366 - CMI #21458 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 02.23.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 75.00 | 48 |  |  |  |  |  | $ 3,600.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,589.78 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 5,189.78 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.02% |  |  |  |  |  |  |  | $ 103.79 |
| Grand Total |  |  |  |  |  |  |  | $ 5,293.57 |