Emergency:

Chillers off in building 356 and in high suction cut off.

Found Trane air cooled chiller off on hi-suction temperature.

Recommend replacement of liquid line drier cores which haven't been changed since original installation along with re-placement of both suction temperature sensors, must add refrigerant since there will be a loss of charge, also both sensors will have to be re-programmed in machine.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Chillers off in building 356 |  |  |  |  |  |  |  |  |
| CSS #93067 - CMI #21778 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 04.20.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 8 |  |  |  |  |  | $ 800.00 |
| 1.1 Labor |  |  |  |  | $ - | $ - | $ - | $ 1,280.00 |
| Computer programmer |  |  |  |  |  |  |  |  |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,574.40 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 3,654.40 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |

| 2.1 Incurred |  |  |  |  |  |  |  | $ 400.00 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2.2 CE Factor 1.02% |  |  |  |  |  |  |  | $ 81.08 |
| Grand Total |  |  |  |  |  |  |  | $ 4,135.48 |