Reports both AHU's are not functioning properly, And the chiller is not holding an ambient temperature

Proposal to:

Diagnostic – received emergency service call.

Checked out Trane outdoor liquid chiller – 100 ton. Found 2 compressors going off on high suction pressure. Adjusted refrigerant charge on circuit #1. head pressure was at 400 pounds at 75-degree outdoor temperature. Adjusted refrigerant charge to 325 which is normal for 75-degree outdoor temperatures. Circuit #2 machine goes off on alarm for high suction temperature. Spoke to factory recommend changing liquid line filter dryers and suction pressure sensor. After those 2 things are changed, we can go from there.

Spoke to Trane and they recommended maintenance and to change liquid line filter dryers.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Reports both AHU's are not functioning |  |  |  |  |  |  |  |  |
| CSS # - CMI #9765 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 08.19.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 150.00 | 12 |  |  |  |  |  | $ 1,800.00 |
| 1.2 Materials |  |  |  |  | $ - | $ - | $ - | $ 1,444.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 3,244.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ 350.00 |
| 2.2 CE factor 1.03% |  |  |  |  |  |  |  | $ 107.82 |
| Grand Total |  |  |  |  |  |  |  | $ 3,701.82 |