Repair generator, showing "low water temperature" error.

Scope of work involved at Rotterdam USARC CSS1199   W/O 18241

- Generator needs complete service. Last Service date was in 2020.

- Unit coolant temperature sensor is faulty causing unit to be inoperable during normal weekly exercise of unit & under Emergency back-up activation.

- Provide complete service and repairs/replacement of parts.

| Provide complete service/ repairs of Kohler Gas Generator |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Remove engine oil & replace with synthetic oil |  |  |  |  |  |  |
| Remove engine coolant, flush, replace coolant |  |  |  |  |  |  |
| Remove & replace Spark plugs |  |  |  |  |  |  |
| Remove & replace air cleaner element |  |  |  |  |  |  |
| Remove & replace worn V-belt |  |  |  |  |  |  |
| Remove & replace radiator coolant sensor relay to controller |  |  |  |  |  |  |
| Check out all electrical terminations on unit. |  |  |  |  |  |  |
| Inspect Automatic Transfer Switch for proper operation |  |  |  |  |  |  |
| Run generator for proper operation |  |  |  |  |  |  |

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY059 |  |  |  |  |  |  |  |  |
| Repair generator |  |  |  |  |  |  |  |  |
| CSS #1199 - CMI #18241 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 06.28.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 110.00 | 12 |  |  |  |  |  | $ 1,320.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,384.53 |
| 1.2 Material 20% markup |  |  |  |  | $ - | $ - | $ - | $ 276.90 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,981.43 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.03% |  |  |  |  |  |  |  | $ 89.44 |
| Grand Total |  |  |  |  |  |  |  | $ 3,070.87 |