Repair Heat Pump #2-26 and Heat Pump #2- 33. Both units are not running nor communicating with building controls.

Proposal to repair Heat Pump 2-26

The scope of our work will include materials and labor for the following:

 Pump down refrigerant and isolate heat pump

 Disconnect Trane control System from heat pump

 Remove heat pump from ceiling and leak search

 Fix minor leak and make note of major leaks.

 Re-install system in ceiling

 Test and place system back into normal operation

Proposal to repair Heat Pump 2-33

The scope of our work will include materials and labor for the following:

 Pump down refrigerant and isolate heat pump

 Disconnect Trane control System from heat pump

 Remove heat pump from ceiling and leak search

 Remove and replace compressor and relay

 Re-install system in ceiling

 Nitrogen pressure test and charge with fresh refrigerant

 Test and place system back into normal operation

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Repair Heat Pumps 2-26 / 2-33 |  |  |  |  |  |  |  |  |
| CSS #26032 - CMI # 9750 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 9.10.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| Heat Pump 2-26 |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 158.11 | 18 |  |  |  |  |  | $ 2,846.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 254.00 |
| Heat Pump 2-33 |  |  |  |  |  |  |  |  |
| 1.3 Labor | $ 158.11 | 36 |  |  |  |  |  | $ 5,506.00 |
| 1.4 Material |  |  |  |  | $ - | $ - | $ - | $ 941.00 |
| 1.5 Misc |  |  |  |  |  |  |  | $ 1,175.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 10,722.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |

| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ 450.00 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 2.2 CE Factor 1.03% |  |  |  |  |  |  |  | $ 335.16 |
| Grand Total |  |  |  |  |  |  |  | $ 11,507.16 |