Repair unit heater in mailroom. No heat in mail room. Thermostat reads CH05, which indicates communication error with split unit.

Proposal to:

* Recover refrigerant from server room unit

*Remove and replace outside condenser with Samsung

* Remove and replace air handler with new updated Samsung unit

* Install new line set

* Evacuate and charge unit with refrigerant

* Reconnect to existing electrical (replace whip, disconnect, and install phase monitor)

* Provide equipment start up, refrigerant charge, and commission as per manufacturer’s specs

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over and Above |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Repair unit heater in mailroom. |  |  |  |  |  |  |  |  |
| CSS #29095 - CMI #14925 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 11.12.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 165.00 | 20 |  |  |  |  |  | $ 3,300.00 |
| 2 techs 10 hours each |  |  |  |  |  |  |  |  |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 3,833.00 |
| 1.2 Piping/Electrical |  |  |  |  | $ - | $ - | $ - | $ 750.00 |
| 1.3 Freight |  |  |  |  |  |  |  | $ 275.00 |
| 1.4 Misc |  |  |  |  |  |  |  | $ 242.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 8,400.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE factor .9% |  |  |  |  |  |  |  | $ (840.00) |

| Grand Total |  |  |  |  |  |  |  | $ 7,560.00 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |