While tech was on site he was asked to look at - compressor is bad and needs to be replaced.

Main Bldg HVAC for the office space.

Tech looked at it and found the compressor is bad and needs to be replaced.

Proposal to:

Garage Office - Compressor serving outdoor condensing unit # RAC17L18B21SA/S# W1H8094039 Necessary reclamation and proper disposal of refrigerant as per EPA regulations

Necessary refrigerant piping to existing

Necessary replacement of liquid line drier

Necessary installation of suction line drier

Necessary acid test

Necessary power and control wiring to existing

Necessary nitrogen purge

Necessary evacuation and system recharge

Necessary start up and test of new compressor

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY050 |  |  |  |  |  |  |  |  |
| compressor is bad |  |  |  |  |  |  |  |  |
| CSS #32387 - CMI #14855 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 09.07.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 163.00 | 9 |  |  |  |  |  | $ 1,467.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 2,804.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 4,271.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 291.50 | 1 |  |  |  |  |  | $ 291.50 |
| 2.2 CE Factor 1.03% |  |  |  |  |  |  |  | $ 136.87 |
| Grand Total |  |  |  |  |  |  |  | $ 4,699.37 |