Repair HVAC Boiler # 1 & 3 on second floor of USARC. Units are locking out on outlet temperature errors. Units have been reset multiple times, but boiler returns to "Locked Out" mode.

Proposal to: Replace failed pump, strainer gasket and chemically clean 3 boilers, install shot feeder, circulate cleaner thru system, install solid chemical shots.

- Isolate & remove failed pump

- Furnish & install replacement pump

- Isolate & chemically clean 3 boilers

- Install shot feeder system into boiler loop system

- Circulate chemical though loop for 4 hours

- Drain & flush loop

- Refill loop & add Corguard solid shots to loop for added protection

- Test operations

- Put units back into service

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Repair HVAC Boiler # 1 & 3 |  |  |  |  |  |  |  |  |
| CSS #90831- CMI #20186 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 11.21.22 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 120.00 | 54 |  |  |  |  |  | $ 6,480.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 5,455.14 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 11,935.14 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred |  |  |  |  |  |  |  | $ 350.00 |
| 2.2 CE Factor .9% |  |  |  |  |  |  |  | $ (1,228.52) |

| Grand Total |  |  |  |  |  |  |  | $ 11,056.62 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |