AFRC HVACs not working properly or not working at all. HVACs 3,4 & 7 are either not functioning properly or nor working at all. Units 3 & 4 are not receiving chilled water and unit 7 is completely inoperable.  HVAC control computer in room 101A is completely inoperable as well.

This proposal is a 3-part proposal:

Please see the vendor proposal for more descriptions of the repairs.

First part is to:

The scope of our work will include materials and labor for the following:

 Provide (1) Delta Controls enteliWEB

o Provide new HTML5 graphics

 Provide Rev 3.40 firmware upgrade for 62 controllers

 Review DDC programming and modify as needed for proper operation

o Includes alarm configuration

 Review existing VFD programming and modify as needed for proper operation

 Provide up to 4 hours training

 Provide 1-year warranty on labor and material

The second part is to:

* Remove and replace failed OEM contactor

The third part is optional:

Add Alternate 1: Substitute Tridium JACE for the enteliWEB software

Provide (1) Niagara 4 JACE

- o Provide Tridium based graphics

o Configure existing alarms to annunciate via the JACE

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over and Above |  |  |  |  |  |  |  |  |
| NY116 |  |  |  |  |  |  |  |  |
| AFRC HVACs not working properly |  |  |  |  |  |  |  |  |
| CSS #21374 - CMI # 5621 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 01.10.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| Delta Controls BMS |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 152.31 | 260.5 |  |  |  |  |  | $ 39,675.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 4,170.00 |
| 2. Repair Cost |  |  |  |  |  |  |  |  |
| Remove & replace OEM contactor |  |  |  |  |  |  |  |  |
| 2.1 Labor |  |  |  |  |  |  |  | $1,262.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 45,107.00 |
| 3. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| CE Factor.9% |  |  |  |  |  |  |  | ($4,510.70) |
| Grand Total |  |  |  |  |  |  |  | $ 40,596.30 |
| **Alternative |  |  |  |  |  |  |  |  |
| Add $9,590.00 to base project price |  |  |  |  |  |  |  |  |