Insulation has been removed from a section of pipes and fittings above AHU-4 (see attached photo) and water dripping from the pipe is infiltrating into the supply fan section of the AHU. The pipe shows significant rust, indicating significant moisture existed prior to insulation removal. There is also considerable condensation visible. Additionally, there is no evidence of glycol in the water that entered the AHU.

Proposal to provide necessary labor & material to replace & repair Victaulic pipe fittings and associated insulation to fix water leaks above AHU 4 including glycol percentage test.

Includes:

- Victaulic wye strainer, butterfly valve and fittings

- Dielectric nipple and copper pipe including fittings

- Necessary pipe insulation

- Glycol percentage test – if system needs additional glycol it will be added to the charge

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY116 |  |  |  |  |  |  |  |  |
| Insulation has been removed from a section of pipes |  |  |  |  |  |  |  |  |
| CSS # - CMI #9748 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 08.05.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 161.00 | 16 |  |  |  |  |  | $ 2,576.00 |
| 2 techs 8 hours each |  |  |  |  |  |  |  |  |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 3,856.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 6,432.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.03% |  |  |  |  |  |  |  | $192.96 |
| Grand Total |  |  |  |  |  |  |  | $ 6,624.96 |