Repair Eaton/Culter-Hammer Clipper Power System 200 kA Surge Protection Devices in both 1st and 2nd floor Circuit Boxes (Room 121 and Room 258). Both surge protectors display single phase faults normally caused by blown fuses

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY116 |  |  |  |  |  |  |  |  |
| Surge Protection Devices in both |  |  |  |  |  |  |  |  |
| CSS # - CMI # 9752 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 08.04.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 100.00 | 24 |  |  |  |  |  | $ 2,400.00 |
| 2 tech 12 hrs each |  |  |  |  |  |  |  |  |
| 1.2 Custom built Surge protectors |  |  |  |  | $ - | $ - | $ - | $ 6,934.00 |
| $3467.00 eachx 2 |  |  |  |  |  |  |  |  |
| 1.3 Misc |  |  |  |  |  |  |  | $1,386.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 10,720.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site | $ 100.00 | 3 |  |  |  |  |  | $ 300.00 |
| 2.2 CE Factor 1.03% |  |  |  |  |  |  |  | $330.60 |
| Grand Total |  |  |  |  |  |  |  | $11,350.60 |

See 2nd page for scope of work:

Proposal to remove / replace:

| 1. Remove a Quantity of ( 2 ) faulty Eaton / Cutler Hammer Clipper Power System |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 200KA Surge Protection Devices in 1st Floor & 2nd Floor Electrical rooms. |  |  |  |  |  |  |  |  |
| Existing receptacles in facility are currently subjected to excessive transient voltage spikes from |  |  |  |  |  |  |  |  |
| utility feeders which can cause sensitive electronics to fail due to overload voltages. |  |  |  |  |  |  |  |  |
| 2. Replace a Quantity of ( 2 ) Custom built Eaton / Cutler Hammer Clipper Power |  |  |  |  |  |  |  |  |
| System Surge protection devices in same areas. |  |  |  |  |  |  |  |  |
| 3. Existing devices are obsolete. Manufacturer has the capability to custom manufacturer |  |  |  |  |  |  |  |  |
| OEM replacement units with a 6-8 week lead time. |  |  |  |  |  |  |  |  |
| 4. Work will be done during normal weekday hours, and the electrical system will need to be shut down |  |  |  |  |  |  |  |  |
| for replacement of devices. The USARC will be responsible to coordinate this with the facility for |  |  |  |  |  |  |  |  |
| all security and communication systems impacted by loss of power. |  |  |  |  |  |  |  |  |