No AC in both 1st and 2nd floor server/TR rooms will not cool. AH will turn on but no cooling. Appears that condensing unit outside will not run.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| AC 1st & 2nd floor server room |  |  |  |  |  |  |  |  |
| CSS #20470 - CMI #5094 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 5.14.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 155.00 | 32 |  |  |  |  |  | $ 4,960.00 |
| 2 Journeymen 16 hours each |  |  |  |  |  |  |  |  |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 4,186.00 |
| 1.3 Misc equipment |  |  |  |  |  |  |  | $919.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 10,065.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ 450.00 |
| CE Factor 1.03% |  |  |  |  |  |  |  | $315.45 |
| Grand Total |  |  |  |  |  |  |  | $ 10,830.45 |

The scope of our work will include materials and labor for the following:

• Recover refrigerant

• Remove and replace both compressors and filter drier

• Nitrogen pressure test and charge with fresh refrigerant

• Remove and replace failed crankcase heaters

• Remove and replace failed contactor on Bryant Rooftop

• Test and place system back into normal operation