No AC in 1st server/TR rooms will not cool. AH will turn on but no cooling. Appears that condensing unit outside will not run.

Change order to:

*Pump down refrigerant and isolate Liebert air handler

*Remove and replace both Liebert air handler filter driers

*Re-pressurize system

*Test and place system back into normal operation

** The work for #2 below has been completed, the change order #1 was discovered after the condensing unit was turned on and it was running hot **

Proposal to:
 The scope of our work will include materials and labor for the following:

▪ Remove and replace Liebert condenser and filter drier

▪ Reconnect to existing refrigerant line and electrical

▪ Nitrogen pressure test and charge with fresh refrigerant

Test and place system back into normal operation.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| No AC in 1st floor server |  |  |  |  |  |  |  |  |
| CSS #20470 - CMI # 5094 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 8.24.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 158.11 | 9 |  |  |  |  |  | $ 1,423.00 |
| 1.2 Misc |  |  |  |  | $ - | $ - | $ - | $ 277.00 |
| 2. Work Completed |  |  |  |  |  |  |  |  |
| 2.1 Labor | $ 155.00 | 28 |  |  |  |  |  | $ 4,340.00 |
| 2.2 Liebert Condenser |  |  |  |  | $ - | $ - | $ - | $ 15,491.00 |
| 2.3 Piping / Misc |  |  |  |  |  |  |  | $2,039.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 23,570.00 |
| 3. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 3.1 Incurred cost |  | 450 |  |  |  |  |  | $ 450.00 |
| 3.2 CE Factor |  |  |  |  |  |  |  | $ 720.60 |
| Grand Total |  |  |  |  |  |  |  | $ 24,740.60 |