No AC in both 1st and 2nd floor server/TR rooms will not cool. AH will turn on but no cooling. Appears that condensing unit outside will not run.

Proposal to:
 The scope of our work will include materials and labor for the following:

▪ Remove and replace Liebert condenser and filter drier

▪ Reconnect to existing refrigerant line and electrical

▪ Nitrogen pressure test and charge with fresh refrigerant

Test and place system back into normal operation.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| No AC in both 1st and 2nd floor server |  |  |  |  |  |  |  |  |
| CSS #20470 - CMI # 5094 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 06.08.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 155.00 | 28 |  |  |  |  |  | $ 4,340.00 |
| 1.2 Liebert Condenser |  |  |  |  | $ - | $ - | $ - | $ 15,491.00 |
| 1.3 Piping / Misc |  |  |  |  |  |  |  | $1,794.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 21,625.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor |  |  |  |  |  |  |  | $ 648.75 |
| Grand Total |  |  |  |  |  |  |  | $ 22,273.75 |