No AC in both 1st and 2nd floor server/TR rooms will not cool. AH will turn on but no cooling. Appears that condensing unit outside will not run.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| 2nd floor Server Room |  |  |  |  |  |  |  |  |
| CSS #20470 - CMI #9766 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 8.19.20 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 142.18 | 32 |  |  |  |  |  | $ 4,500.00 |
| 1.2 Liebert condenser |  |  |  |  | $ - | $ - | $ - | $ 7,172.00 |
| 1.3 Misc |  |  |  |  |  |  |  | $1,355.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 13,027.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ 1,423.00 |
| 2.2 CE Factor 1.03% |  |  |  |  |  |  |  | $ 383.50 |
| Grand Total |  |  |  |  |  |  |  | $ 14,883.50 |

The scope of our work will include materials and labor for the following:

 Remove and replace Liebert condenser and filter drier

 Reconnect to existing refrigerant line and electrical

 Remove and replace interior filter driers

 Nitrogen pressure test and charge with fresh refrigerant

 Test and place system back into normal operation