HW pump #4 is squealing in first floor mechanical room. Condensate lines behind boiler #1 are rotted off and leaking onto the floor.

Inspected Circ pump #4 – Found Bad bearings

Proposal – remove pump #4 and replace bearings.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| HW pump #4 is squealing in first floor |  |  |  |  |  |  |  |  |
| CSS #25073 - CMI #12850 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 4.22.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 124.00 | 12 |  |  |  |  |  | $ 1,488.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,221.71 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,709.71 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE factor 1.03% |  |  |  |  |  |  |  | $ 81.29 |
| Grand Total |  |  |  |  |  |  |  | $ 2,791.00 |