Repair Chiller, Building is very warm.
Unit does not stay running. Water temperature drops very low when unit is reset and it trips out on safety. Potential bad temperature probe.:

Proposal to:

- Service to building chiller

- Found existing temp sensor has failed

- Pressures running very low

- Leak tested chiller and found no clear signs of leak

- Furnish and install (2) new temperature sensors

- Recharge with new refrigerant

- Start up and operational test

- Put units back into service

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| Repair Chiller, Building is very warm |  |  |  |  |  |  |  |  |
| CSS #94024 - CMI #23322 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 07.24.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 120.00 | 16 |  |  |  |  |  | $ 1,920.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,071.07 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 2,991.07 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred Cost |  |  |  |  |  |  |  | $ 480.00 |
| 2.2 CE Factor 1.02% |  |  |  |  |  |  |  | $ 69.42 |

| Grand Total |  |  |  |  |  |  |  | $ 3,540.49 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |