| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| PA051-01 Johnstown |  |  |  |  |  |  |  |  |
| Oil/water separator at Building 292 is in high oil level alarm |  |  |  |  |  |  |  |  |
| CSS #16562 - CMI # 6832 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 12.24.18 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 121.41 | 9 |  |  |  |  |  | $ 1,092.69 |
| 1.2 Tank Monitoring Panel |  |  |  |  | $ - | $ - |  | $ 2,390.00 |
| 1.2 A Mark up on Panel |  |  |  |  |  |  |  | $ 525.66 |
| 1.3 Corrosion Inhibitor |  |  |  |  |  |  |  | $193.31 |
| 1.4 Shipping |  |  |  |  |  |  |  | $ 45.00 |
| 1.5 Service Truck Charge |  |  |  |  |  |  |  | $ 85.47 |
| 1.6 Consumables |  |  |  |  |  |  |  | $ 200.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 4,532.14 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Previously Approved |  |  |  |  |  |  |  | $ 1,706.76 |
| CE Factor 102% |  |  |  |  |  |  |  | $ 124.77 |
| Grand Total |  |  |  |  |  |  |  | $ 6,363.67 |

Oil/water separator at Building 292 is in high oil level alarm. The oil in the separator must be pumped out to ensure the system continues to work correctly and to ensure no illicit discharge of oil occurs, which may result in a notice of violation (NOV) and/or a fine. Water must be put back into OWS for proper operation.

When site was visited tech found ASF & tested the components of the monitoring system. Found that the Panel was burnt out internally, please see attached video.

Proposal is to de-energize & dissemble the existing panel & disconnect from the 3 conduits, the probes & sensors will be removed from the tank. The new panel will be installed , & the leak & 2 oil level probes will first be tested to ensure the components all work properly before reinstallation. When previously on site we removed & attempted to test the 3 probes but the panel was completely unresponsive.

While the leak probe is out of the interstice, we will add corrosive inhibitor to the space to neutralize any residual condensation/water & arrest corrosion potentially underway or that could develop.