** Emergency Call **

Repair roof ruptured heating coil at building #354. Coil must have frozen during power outage.

Emergency service call --- office air handler coil split from loss of power causing outside air damper to stay-open with freezing outdoor conditions.

Scope of work:

Disconnect supply and return lines from air handler heating coil , disconnect freeze stat from existing coil, remove all support brackets securing coil, remove coil from existing air-handler, Braze and repair existing coil could not get new coil to fit this air-handler for 6 weeks recommend repairing existing coil also, I would recommend  adding Glycol to entire heating system, This will be an additional proposal with the same CSS# since the time line for getting glycol will be 2-weeks from this approval, also recommend changing actuator on outside air damper and lubricate outside air damper linkages, Re-place circuit setter and all necessary fittings and Y-type strainer to establish all necessary flow through coil

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY024 |  |  |  |  |  |  |  |  |
| Repair roof ruptured heating coil |  |  |  |  |  |  |  |  |
| CSS #91366 - CMI #20601 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 01.25.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 75.00 | 48 |  |  |  |  |  | $ 3,600.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,156.20 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 4,756.20 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Incurred |  |  |  |  |  |  |  | $ 400.00 |
| 2.2 CE Factor 1.02% |  |  |  |  |  |  |  | $ 103.12 |

| Grand Total |  |  |  |  |  |  |  | $ 5,259.32 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |