Replace the under sized pumps on the 3 Lochinvar heating Boilers. Pumps are
undersized and causing boilers to continuously fault out.

Found during Annual Boiler PM.

Once we got the system cleaned, the flow wasn’t correct. We called in the Lochinvar boiler rep and had him look. He found that the pumps are grossly undersized for the BTU rating of the boilers. That is causing nuisance trip outs of the boilers on high temp

Proposal to:

Isolate and remove improper pumps

Furnish and install replacement pumps

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Replace the under sized pumps |  |  |  |  |  |  |  |  |
| CSS #91354 - CMI #20599 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 02/06/23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 120.00 | 24 |  |  |  |  |  | $ 2,880.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 7,090.49 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 9,970.49 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.02% |  |  |  |  |  |  |  | $ 199.40 |
| Grand Total |  |  |  |  |  |  |  | $ 10,169.89 |