Backflow Preventer - RM 113 – there is a 2 ½ inch Wilkins Model 909MOD, serial # 125642, the 2nd check must be replaced and or cleaned

(2) Backflow leaking from blow off funnel

Isolate and drain water lines

Remove pipe covering as necessary

Furnish and install new backflow repair kits

Pressure test

Replace pipe covering that was removed

Put units back into service

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY128 |  |  |  |  |  |  |  |  |
| Backflow Preventer RM 113 |  |  |  |  |  |  |  |  |
| CSS #595 - CMI #18255 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 01.24.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 115.00 | 40 |  |  |  |  |  | $ 4,600.00 |
| 1.2 Material 2 1/2 check valve |  |  |  |  | $ - | $ - | $ - | $ 1,617.89 |
| 1.2 Material 3 check valve |  |  |  |  | $ - | $ - | $ - | $ 1,884.52 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 8,102.41 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.02% |  |  |  |  |  |  |  | $ 162.04 |
| Grand Total |  |  |  |  |  |  |  | $8,264.45 |