Repair HVAC BMS.

There is no air moving in the building. New Fire Alarm system contractors state that the system shows all normal. AMI reports AHUs and Chiller are in order but not being called for demand. BMS AHU controllers show equipment disabled.

Diagnosis:

I was at the New Windsor site today and diagnosed the air handlers having issues. As suspected, there were bad contactors and fuses on several units. The parts needed are obsolete from both Trane and the part manufacturer, but I was able to come up with suitable replacements which will be quoted out for repairs.

Note: Dave Ogden EMTech does not have programming privileges for the Delta system. He was not able to log into the system at all, but once the repairs are made the AHU's will run on a start command.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Additional Funding |  |  |  |  |  |  |  |  |
| NY116 |  |  |  |  |  |  |  |  |
| Repair HVAC BMS |  |  |  |  |  |  |  |  |
| CSS #93481 - CMI #22727 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 06.12.23 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 163.00 | 8 |  |  |  |  |  | $ 1,304.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 1,540.09 |
| 1.3 Trip |  |  |  |  |  |  |  | $ 353.50 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 3,197.59 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE Factor 1.02% |  |  |  |  |  |  |  | $ 63.95 |

| Grand Total |  |  |  |  |  |  |  | $ 3,261.54 |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |