Repair VAV on second floor in the South-East corner office.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Funding Request |  |  |  |  |  |  |  |  |
| NY060 |  |  |  |  |  |  |  |  |
| Repair VAV on second floor |  |  |  |  |  |  |  |  |
| CSS #30974 - CMI #13347 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 09.15.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 114.00 | 16 |  |  |  |  |  | $ 1,824.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 3,125.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 4,949.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 CE factor 1.03% |  |  |  |  |  |  |  | $ 148.47 |
| Grand Total |  |  |  |  |  |  |  | $ 5,097.47 |

** Found unit had an explosion caused by a hard start kit. It melted most of the wiring as well. Recommend replace unit, that is the safest and most cost-effective solution.

Proposal to:

- Remove the current heat pump which is effectively destroyed

- Replace it with a new Trane water source heat pump

- Test Operation