Fahrenheit Inc.

85 Farless Avenue

Old Bridge, New Jersey 08857

Telephone (732) 673- 9318  E-mail: Celcius60@aol.com

	PROPOSAL
	X

	INVOICE
	

	DIAGNOSTIC
	


Today's Date: 6/10/2021

Customer Name: Joe Bayne



	CSS/INVOICE#
Outdoor Liquid Chiller
	DATE(S) OF SERVICE


	LOCATION

Bldg 358


	JOB DESCRIPTION
troubleshooted bldg 358 outdoor liquid chiller, found open windings on both outdoor condenser fan motor, fan motors not operating, checked voltage to both condenser fan motors, both had correct voltage on all 3 legs. Removed 2 damaged motors from outside condenser, both condenser motors are OEM and has to be purchased from factory. 1 to 3 day lead time

	PARTS
2 HP York OEM Motors Model#02427322-103 frame 56YZ frame and 2 HP motor


	COST
$1764.37 for each motor

TOTAL $3528.74

	LABOR

1 day 2 mechanics @ 150.00 an hour
	COST

$1,200.00

	TAX
	

	TOTAL
	$4,728.74


Thank you for your business


