Over and Above Estimate

Region: 2

Location:  NY024

CSS #:  21273

Maximo Work Order No.: 5614

Date Issued:  9/24/19

Original Description:  Repair MEP and exterior building Lighting.  Noted DES issue
during 7/25/2019 inspection. During a night-time security check and lighting
survey, it was noted about 6 lights in MEP, and several exterior building
lights were inoperable.

Repairs Needed: Building 357:

Trace and locate short ckt. In lighting for exterior garage lights total of six

Remove ballast and lamps and replace with LED wall pack retrofit lamp total of six

Replace photo cell control

Check three high bay fixtures inside garage not operating and remove lamps and disconnect ballast replace with LED style lamp as in other three fixtures.

Building 356:

Check exterior light fixtures over doorways total of four told not operating by Vinny Giordano

Supply and replace 42W triple tube compact fluorescent lamps total of eight

Asset Number:

| Quantity | Line Item Number | Description | Labor Hours | Shipping | Labor | Materials | Tax | Total |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 6 |  | LED HID Replacement lamps |  |  |  |  |  | $540.00 |
| 1 |  | Photo Cell Control |  |  |  |  |  | $42.00 |
| 3 |  | LED replacement lamps for high bays |  |  |  |  |  | $342.00 |
| 16 |  | PL42 Triple tube lamps |  |  |  |  |  | $288.00 |
|  |  | Lamp disposal fee |  |  |  |  |  | $45.00 |

Note: RS Means (Pre-Priced) not used in compiling this estimate.

Note: Subcontractor quote attached.

Estimate Summary:

| Labor Hours | Labor Cost | Material Cost | Tax and shipping | Total Cost | CE Factor | Total Estimate |
| --- | --- | --- | --- | --- | --- | --- |
| 16 @$155.00/MH | $2,480 | $1,257.00 |  | $3,737.00 | 90% | $3,363.30 |

Note: Tax and shipping are included in the materials cost