|  | PROJECT WORK SPESIFICATIONS 99th Readiness Division Directorate of Public Works Fort Dix, New Jersey 08640 |  |
| --- | --- | --- |

11 October 2023

| Project Name: | REPLACE HVAC COMPONANTS: - ROOFTOP UNITS - BOILERS - UPDATE THE BUILDING CONTROL SYSTEM |
| --- | --- |
| Project Number: | FIS# 96036 |
| Project Location: | Pendel-Caminiti USARC (PA027) |
|  | 950 New Castle Road |
|  | Farrell, PA 16121 |

| Project POC: PRI: | RFOS/QAR: Scott Kawski | Wk.: (910) 656-0251 | Cell: (814) 392-6879 |
| --- | --- | --- | --- |
| Project POC/ALT: | AFOS: Cindy Croyle | Wk.: | Cell: (412) 477-7816 |
| Project POC/ALT: | FAC COR: Mr. Steve Hafer | Wk.: (910) 656-0271 | Cell: |
| Project POC/RD: | FET: Donald Bement | Wk.: (910) 656-0252 | Cell: (814) 450-6508 |
| HQ Eng. Tech: |  | Wk.: | Cell: |

11.1. PROJECT SPECIFICATIONS:

11.1.1. Required rtasks

- Remove and replace the 2-each AAON roof top air handling cooling units Model number:  43481 (RK-25-2-EO-222:CK0DHA00D0000X).

  - The units are located on the roof of the second floor.

  - The units shall be replaced with an approved equivalent to the existing.

  - Photos of the data plate and the As-Build Drawing for the units shall be found in the attached HVAC Technical Exhibit.

  - The new units shall be BACnet compatible.

  - The new units shall be compatible and work in as a lead lag system.

  - The Contractor shall preform required calculation in order to appropriately size the new roof top units.

- Remove and replace the 4-each Munchkin Model number:  399M R2 boilers.

  - The boilers shall be replaced with 2-each RIELLO ARRAY or an approved equivalent to the existing.

  - Photos of the data plate and the As-Build Drawing for the units shall be found in the attached HVAC Technical Exhibit.

  - The new boilers shall be of a condensate type.

  - The new boilers shall be BACnet compatible.

  - The new boilers shall be compatible and work in as a lead lag system.

  - The Contractor shall preform required calculation in order to appropriately size the new boilers.

- Update the control by designing and install a new building automation system (BAS).

  - The new controls shall be an Enterprise Building automation System, Niagara N4 front end with REFLOW graphics.

    - The Niagara software shall be the latest version.

  - All data shall be backed up prior to uninstalling the current BAS System.

  - Existing communication cable shall be utilized unless it is found to be deficient.

    - Any deficient communication cable shall be replaced.

  - The new design shall incorporate the OMS building’s appliances and equipment.

    - A conduit raceway has been identified between the two buildings.

      - Old metal fixed-line phone wire shall be removed.

      - New BAS control cable and an additional pull-line shall be installed.

  - The designing engineer shall take note that the heated fin-tube piping runs through coils located in the duct work near the VAV boxes. The new controls shall be designed to allow the interlocking of the rooftop AHUs, VAV boxes, and the heated fin-tube piping.

  - **NOTE** Emergency Shut Down Switches shall be tied directly into the new units and NOT through the building automation system.

11.1.2. Since the tasks associated with this project are located in numerous areas around the facility and the specific tasks identified are different in specific areas. The Contractor shall reference this SOW and the attached HVAC Technical Exhibit for the Work Identification Map/s for each location and the specific tasks. **NOTE** SOW shall supersede the Technical Exhibits. If clarification is required of any item or task, questions shall be directed to the RFOS/COR.

11.1.3. Due to the abondance of information only the minimum has been provided in the HVAC Technical Exhibit. Additional As-Build Drawing and Utility Assessment survey shall be provided the awarded Contractor once the NTP has been authorized.

11.1.4. The new equipment and/or units are required to be:

- Of a Premium efficiency

- Either an Energy Star – or – FEMP-Designated Product.

  - Unless neither is reasonably available.

  - Reasonably available time frame to be determined by the RFOS/COR.

11.1.5. **NOTE** As part of the Tasks associated with this project shall encapsulate, enclose, and/or conceal specific tasks. The Contractor shall see requirements listed in Section 11.10. QUALITY ASSURENCE (QA).

11.1.6. All quantities are estimated. The Contractor shall field verify specifications, dimensions, and quantities prior to ordering material.

11.2. ROOF TOP AIR HANDLING COOLING UNITS

11.2.1. DEMO

11.2.1.1. The Contractor shall lockout/tagout the roof top units as needed for removal.

- The electrical wiring, conduit, and control wiring as need.

11.2.1.2. The Contractor shall remove the lightening arresters and wire.

- Lightening arresters shall be retained and reinstalled.

- Grounding wire shall be disposed of.

11.2.1.3. The Contractor shall remove existing piping and insulation as needed.

11.2.1.4. The Contractor shall remove and dispose of all refrigerants IAW all local, state, and federal laws.

11.2.1.5. The Contractor shall remove and disposes of the 2-each roof top units.

11.2.2. INSTALL AND SERVICE

11.2.2.1. The Contractor shall furnish and install 2-each roof top air handling cooling units as listed above in section 11.3.

- The new roof top units shall be installed utilizing the existing support brackets and mounting system.

11.2.2.2. The Contractor shall perform all installation per manufacturers’ specification.

11.2.2.3. The Contractor shall furnish and install or modify as required:

- Electrical wiring, conduit, and control wiring.

- Piping and Insulation.

  - 2-inch minimum fiberglass insulation with jacket.

- Pipe labeling as required.

11.2.2.4. The Contractor shall reinstall the retained lightning arresters.

11.2.2.4.1. The Contractor shall furnish and install new grounding wire.

- Approximately 150-linear-feet of grounding wire shall be required.

11.2.2.5. The Contractor shall verify and confirm that there are no leaks in the system and correct any deficiencies as required.

11.2.2.6. The Contractor shall integrate the roof top units into the building automation system and verify communication.

11.3. BOILERS

11.3.1. DEMO

11.3.1.1. The Contractor shall isolate and drain the glycol from the boiler system and existing piping.

11.3.1.2. The Contractor shall chemically clean the entire closed loop heating system ensuring all control valves are locked in fully open position to ensure flow through all terminal units and circulate for 24 hours minimum or as recommended by chemical supplier. The details of proposed cleaning chemical shall be provided during submittal.

11.3.1.3 The Contractor shall flush the entire closed loop heating system and use proper disposal methods as mandated by all Local, State and Federal laws and regulations.

11.3.1.4. The Contractor shall containerize all chemically treated washing agent and characterize it as required in 40 CFR 262.11.  The results of this determination shall be submitted to the 99th Readiness Division, Environmental for review prior to disposing of the waste.  If the waste is determined to be a hazardous waste, it shall be containerized in a DOT approved container for shipment and will remain on-site.  The 99th Readiness Division will dispose of any hazardous waste that is generated and the contractor will dispose of any non-hazardous waste that is generated.

11.3.1.5. The Contractor shall disconnect the boilers from the Fire Alarm System.

11.3.1.6. The Contractor shall lockout/tagout boilers as needed.

- The gas service to the boilers and disconnect gas pipelines.

- The electric, conduit, and control wiring as need.

11.3.1.7. The Contractor shall remove existing pipes and insulation as needed.

- Glycol distribution piping.

- Intake and exhaust pipes.

- Condensate drains and all associated hardware.

11.3.1.8. The Contractor shall remove and dispose of 4-each booster pumps.

11.3.2. INSTALL AND SERVICE

11.3.2.1. The Contractor shall furnish and install 2-each boiler units as listed above in section 11.3.

- The new boiler units shall be installed on the existing raised concrete pads.

11.3.2.2. The Contractor shall perform all installation per manufacturers’ specification.

11.3.2.3. The Contractor shall furnish and install all piping and pipe fittings to connect any of the existing item to the new boilers as required, but not limited to:

- Glycol distribution piping.

- Hot water distribution

- Hot water bypass blowoff piping.

11.3.2.4. The Contractor shall furnish and install 4-each new booster pumps inline circulation pumps. New pumps shall be of the same make, model or equivalent to that that was removed.

11.3.2.5. The Contractor shall furnish and install approximately 125-linear-feet of 6” PVC air intake and exhaust piping and clamps IAW manufactures recommendations and industry standards with the new boiler system.

11.3.2.6. The Contractor shall furnish and install an approved condensate and drain line running from each of the new boilers to the existing floor drain. Each condensate drain line to include an inline Condensate Neutralizer.

11.3.2.7. The Contractor shall inspect and verify the valve operation in the hot water and supply water circuits for boiler, validate functionality of valves and controls by presenting boiler can and does function per manufactures specifications.

11.3.2.8. The Contractor shall fill and purge the system of any air.

- System to be filled with an approved water glycol mixture.

- All air shall be purged from the system.

- Contractor shall verify there are no leaks in the new boiler system and correct any leaks as required.

11.3.2.9. The Contractor shall furnish and install pipe insulation.

- To include the various fittings and elbows

- Pipe insulation shall be a minimum of 2-inch fiberglass with a service jacket.

11.3.2.10. The Contractor shall furnish and install all required labels noting the following examples, but not limited to:

- Label all system valves and ensure nomenclature in the building automation system is the same.

- Label hot water piping for water type and direction.

- Shut offs.

- Any other pertinent and/or required information.

11.3.2.11. If any of the existing connections require relocation the existing penetrations shall be sealed to match the surrounding surfaces to restore them back to the original appearance.

11.3.2.12. If any of the existing connections shall be terminated:

- The existing penetrations shall be sealed to match the surrounding surfaces to restore them back to the original appearance.

- The existing connections shall be terminated and secured IAW industry standards.

11.3.2.13. The Contractor shall verify and confirm that there are no leaks in the system and correct any deficiencies as required.

11.4. BUILDING AUTOMATION SYSTEM

11.4.1. DEMO

11.4.1.1. The Contractor shall make a backup of the entire existing HVAC control system. All backup files shall be provided to the COR/RFOS during closeout of the project.

11.4.1.2. The Contractor shall remove and properly dispose of the existing building automation system, including, but not limited to all sensors, actuators, network cable as needed, relays, and other components. Labeling from all wiring, sensors, actuators, inputs, and outputs and maintain for future use. Any identified inoperable devices shall be reported to the RFOS/COR in writing.

11.4.1.3. The Contractor shall create opening to install BAS control cabling.

- Opening that may be required:

  - Penetrations through concrete, brick and/or block walls.

  - The Contractor shall only make openings as needed. If an opening already exists, it shall be utilized. (IE. old fixed-line phone wire raceways)

  - NO penetrations shall be authorized into or through the vault.

11.4.1.4. The Contractor shall demo and remove 2-each fixed-line metal phone wire cables from the conduits leading from the mechanical room of the training building to the storage area above the OMS buildings office.

- The black communications wire shall remain in the conduit.

- Additional fixed-line phone wire may be removed to as needed to install BAS control cable with out making a new opening.

- An approximate 750-linear-feet of fixed-line phone wire shall be removed.

11.4.2. INSTALL AND SERVICE\

11.4.2.1. The Contractor shall design and install a fully functional building automation system.

11.4.2.2. The Contractor shall license, install, and utilize the Niagara Modules ReFlow Site module for all system graphics. All point names, point histories, and alarms shall utilize the USAR EBCS Point Naming Convention and ReFlow graphic design standard.

11.4.2.3. The Contractor shall set up all trends, alarms, and scheduling, and graphics to meet USAR EBCS naming convention (see attachment G) and graphics standards. The Contractor shall provide a sample of the graphics display prior to programming and installation. The Contractor shall license and install Niagara Modules ReFlow module and shall reconstruct all local Niagara graphics utilizing the ReFlow module.

11.4.2.4. The Contractor shall furnish and install DDC/building equipment controllers for control and monitoring of the following equipment:

- Training Center Building:

- 7-each Cabinet Unit Heaters.

- 2-each Make-up Air Unit (Kitchen & Drill Hall).

- 1-each Heating Ventilator (Kitchen).

- 1-each Hot Water Heating System including:

  - 2-each Boilers and the individual heat exchangers.

  - 7-each Circulating Pumps.

- 2-each Domestic Hot Water Heater (monitor only).

- 2-each Roof Top Unit.

- 43-each Variable Air Volume Units:

  - 24-each on the 1st floor.

  - 19-each on the 2nd floor.

- 14-each Split unit (monitor only).

- 8-each Exhaust Fan.

- 3-each Fan Coil.

- 1-each Co2 Alarm (Mechanical room)

- Utility Meters:

  - 1-each Electrical Meter.

  - 1-each Water Meter.

  - 1-each Gas Meter.

- OMS Building

- 1-each Split unit (monitor only)

- 1-each Domestic Hot Water Heater (monitor only)

- 4-each Unit Heaters (monitored only)

  - 2-each one in each work bay

  - 2-each in the mezzanine/storage area above the toolroom and latrine

  - **NOTE** the 2-each Unit Heaters that are “RED LINED” shall not be included in the control.

- All building controls shall be programmable/configurable through the Niagara workbench software.

11.4.2.4.1. Air Handling Unit controls shall include, at a minimum, the following hardware control points: exhaust air damper command (%), exhaust air flow (cfm), return air flow (cfm), return air temperature (F), return air CO2 (ppm), return fan command (start/stop), return fan speed (%), return relative humidity (%), outside air damper command (%), outside air flow (cfm), mixed air temperature (F), filter status (pressure differential), supply fan command (start/stop), supply fan command speed (%), Hot water valve (%), chilled water valve (%), supply air temperature (F), duct static pressure (in/wc).

11.4.2.4.2. All Variable Air Volume (VAV) controls shall include, at a minimum, the following hardware control points: damper position (%), hot water valve (%), discharge air temperature (F), zone temperature (F), zone occupancy (PIR).

11.4.2.4.3. Split unit controls shall include, at a minimum, the following hardware control points: zone temperature (F), zone occupancy (PIR), return air temperature (F), supply air temperature (F), supply fan command (start/stop), hot water valve (open/close), DX cooling enable (on/off). Integration shall include heating, cooling, make up air and all other available read and write points.

- The split units have wall mounted thermostats that are prewired back to the Mechanical Room.

- The split system shall be monitored for operation only.

- No email notifications are required for the split units.

11.4.2.4.4. Exhaust fan controls shall include, at a minimum, the following hardware control points: exhaust fan command (on/off) (if already controlled by existing BCS), exhaust fan status (on/off). Exhaust fans that are currently controlled by manual switch shall remain manually controlled and shall be monitored for status only.

11.4.2.4.5. Make Up Air (MAU) unit controls shall include, at a minimum, the following hardware control points: outside air damper status (open/closed), filter status (differential pressure), supply fan status (on/off), burner status (on/off), freeze stat, supply air temperature (F), zone temperature (F). The freezestat shall be resettable through the building automations interface.

11.4.2.4.6. The training building hot water system controls shall include, at a minimum, the following hardware control points: outside air temperature (F), outside air humidity (%), HW supply temperature (F), HW return temperature (F), HW loop differential pressure, HW pump command (on/off), HW pump status (on/off), HW pump speed (%), VFD alarm, boiler isolation valve command (open/closed), boiler enable (on/off), boiler alarm.

11.4.2.4.7. The OMS building hot water system controls shall include, at a minimum, the following hardware control points: outside air temperature (F), outside air humidity (%), HW supply temperature (F), HW return temperature (F), hot water valve 1 command (%), hot water valve 2 command (%), HWP1 command (on/off), HWP1 status (on/off), loop 1 pump command, loop 1 pump status, loop 1 return temperature, loop 2 pump command, loop 2 pump status, loop 2 return temperature (F), smoke alam/FACP status, and emergency shutdown status.

11.4.2.4.8. Fan Coil Unit controls shall include, at a minimum, the following hardware control points: zone temperature (F), zone occupancy (PIR), fan command (on/off), fan status (on/off), cooling enable (on/off), heating enable (on/off), supply air temperature (F), return air temperature (F),

11.4.2.4.9. All unit heaters shall be controlled by communicating thermostat style zone temperature controllers. The zone temperature controls shall have zone temperature sensor, occupancy override button, PIR sensor, fan status, and relative humidity sensor at a minimum. The communicating thermostats shall utilize BACnet for communication with the JACE.

11.4.2.4.10. The Contractor shall furnish and install approximately 100-each new zone temperature/humidity sensors with displays to replace all existing thermostats. Contractor shall set all thermostat allowable setpoint ranges to 68-74 degrees Fahrenheit.

- Approximately 95-each throughout the training building.

- Approximately 5-each throughout the OMS building.

11.4.2.5. The Contractor shall furnish and install all enclosures, wiring, relays, and sensors as required.

11.4.2.6. The Contractor shall furnish and install copper conductor wire as needed.

- New wire shall be sized appropriately for power demand and use.

  - Stranded, PVC jacket, #24, 4 pair, category 5e.

    - Approximately 500-linear-feet.

  - Stranded, PVC jacket, #24, 4 pair, category 6.

    - Approximately 500-linear feet.

  - Fiberoptic cable:

    - Approximately 250-linear-feet.

- Wiring to be installed in accordance with NEC guidelines.

11.4.2.7. The Contractor shall build lead/lag sequence for boilers and circulator pumps. Sequence shall be based on run hours and shall have automatic fail-over in the event of boiler or pump failure.

11.4.2.8. The Contactor shall design HW system to enable when outside air temperature falls below 55F (adjustable) and disable when outside air temperature rises above 60F (adjustable).

11.4.2.9. The installed control system shall control all heating and cooling zones based upon occupied and unoccupied heating and cooling setpoints. Standard setpoints shall be 55F unoccupied heating, 68F occupied heating, 80F unoccupied cooling, 76F occupied cooling. All setpoints shall be fully adjustable from the operator interface.

11.4.2.10. The installed control system shall utilize hand-off-auto style relays for all start/stop functions of secondary hot water system pumps and boilers.

11.4.2.11. The Contractor shall install two (2) CAT6 network drops to connect the AMSA JACE to the Army Reserve Network (ARNET). The cabled shall be violet in color to differentiate from other building communications wire and shall be labeled with function and destination at each end. The 2nd network drop shall remain disconnected to serve as backup connection.

11.4.2.12. The Contractor shall furnish and install 1-each new Windows 10 PC to function as a local operator workstation. The computer shall be Windows 11 ready. Access to the Niagara system shall be through web browser only. Niagara supervisor software should not be installed. The RFOS shall determine desired location for workstation.

11.4.2.13. The Contractor shall implement demand control ventilation (DCV) and optimum start/stop (OSS) algorithms in all airside equipment. DCV shall be based upon return air CO2.

11.4.2.14. The Contractor shall implement humidity control strategy using return air humidity sensors, zone temperature sensors, outside air temperature sensors, and outside air humidity sensors in each AHU. Humidity control strategy will limit economizer function in order to maintain zone humidity less than 50% (adjustable).

11.4.2.15. Prior to purchase and installation of any control components, the Contractor shall provide a full submittal package consisting of proposed network diagram, proposed sequence of operations, and hardware specifications for government approval.

11.4.2.16. Upon project completion, the Contractor shall provide a copy of DDC system As-Build including network diagram, sequence of operations, parts list, and full points list. The Contractor shall also provide a backup copy of all software, program files, and the Niagara station on CD/DVD or communicated electronically.

11.4.2.17. The Contractor shall replace any additional deficient temperature sensors, pressure transducers, damper/valve actuators, status signals, CO2 sensors, relays, or any other input/output deemed inoperable.

11.4.2.18. The Contractor shall furnish and install a BACnet/IP trunk via CAT-6 wiring to link all controllers into the BACnet network. Contractor shall terminate BACnet network onto existing.

Niagara Jace-8000, located in first floor mechanical room. Contractor shall verify network.

communication of all devices on BACnet/IP trunk, first at each device, and subsequently at the JACE front end.

11.4.2.19. The Contractor shall provide KMC Converge 3rd Party Driver to the JACE 8000 to allow for full programming compatibility at the Jace and Workbench software platform.

11.4.2.20. The Contractor shall fully commission each system via point-to-point checkout, which shall.

include step testing of all analog actuators. Contractor shall keep and maintain all point-to-point.

checkout sheets and submit to government during closeout phase of project.

11.4.2.21. The Contractor shall update the existing Niagara Software Maintenance Agreement to a five (5) year SMA.

11.5. UPON COMPLETION

11.5.1. The Contractor shall energize the system with electrical power at the Main Panel and perform startup test procedures on all the newly installed equipment and components to ensure proper functioning.

11.5.2. The Contractor shall backfill, level, and spread grass seed to any area that require restoration. To fill wheel ruts caused by a crane.

- All new seeded areas shall be mulched with straw or an approved material.

11.5.3. The Contractor shall furnish all materials to seal any/all penetrations and/or openings.

- To include interior and exterior edges of door frames and the area where the door frame meets the threshold.

- Opening shall be sealed IAW the best Standard Industry Practice

- Similar in color to the surrounding

- And shall be water and rodent proof.

11.6. TRAINING & SUPPORT

11.6.1. The Contractor shall instruct building staff, AFOS and RFOS/COR personnel on Manufacturer’s O&M requirements and provide training of full system functionality per contract specifications at time of project conclusion.

11.7. COMMISSIONING

11.7.1. The Contractor shall provide full testing, startup, and provide a detailed report of testing and startup of all building automation system components and connected equipment. All deficiencies found in newly installed equipment shall be corrected at no added expense to the government, while all deficiencies of pre-existing equipment shall be noted for repair outside the scope of this project.

11.7.2. The Contractor shall hire an official factory field representative of the installed equipment and components installed to be a 3rd party commissioning agent. The commissioning agent shall operate and verify, testing and commissioning of the installed equipment. A full commissioning report shall be provided to the government upon completion of commissioning. The manufacturing companies' startup, testing and commissioning forms shall be used to record this information. Information that shall be reported to include, but not limited to is electrical voltages, burner manifold pressures, gas supply pressure, water pressure and temperatures, and combustion analysis. Contractor shall provide the COR with all testing and commissioning forms and shall provide labor to perform commission testing with 3rd party agent as required.

11.7.3. Upon commissioning of the components installed, the Contractor shall program all heating and cooling set points at the following:  administrative areas shall have an occupied heat setting of 68 f. and unoccupied setting of 55 f.  Cooling, occupied setting of 76 f. and unoccupied set point of 85 f.

11.7.4. The Contractor shall lock all set points once they are properly programmed. The Contractor shall then verify all control points are operating properly and recording within the standard parameters. The

11.8. WARRANTY

11.8.1. The Contractor shall provide documentation to the duration of time the Standard Manufacturer’s Warranty extends to for all new equipment, materials, and/or components being installed.