During seasonal change over technician found that the temperature sensor is faulty and needs to be replaced.

| CMI Cost Estimate |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Over & Above |  |  |  |  |  |  |  |  |
| NY116 |  |  |  |  |  |  |  |  |
| Found during Seasonal Changeover |  |  |  |  |  |  |  |  |
| CSS #30609 - CMI #12877 |  |  |  |  |  |  |  |  |
| Prepared By: J. Bayne |  |  |  |  |  |  |  |  |
| 6.21.21 |  |  |  |  |  |  |  |  |
|  |  |  | Labor |  |  | Sub | OHP |  |
| Description | Rate | Hours | Cost | Material | Tax | Total | 20% | Total |
| 1. Repair Cost |  |  |  |  |  |  |  |  |
| 1.1 Labor | $ 163.00 | 8 |  |  |  |  |  | $ 1,304.00 |
| 1.2 Material |  |  |  |  | $ - | $ - | $ - | $ 3,188.00 |
| Sub Total Repair Cost |  |  |  |  |  |  |  | $ 4,492.00 |
| 2. Initial Service Call Investigation |  |  |  |  |  |  |  |  |
| 2.1 Field Review at Site |  |  |  |  |  |  |  | $ 207.50 |
| 2.2 CE Factor 1.03% |  |  |  |  |  |  |  | $ 140.98 |
| Grand Total |  |  |  |  |  |  |  | $ 4,840.48 |

5/14 – Initial proposal submitted to replace temperature sensor on the Trane Chiller. Proposal approved on 5/18. Tech arrived on site 6/07 with new sensors and attempted to replace.

Tech found that the new sensors are not compatible with the very old controller in the unit.

6/21 Proposal to replace the existing controller / sensors for the Trane Chiller.

- Replace temperature sensor on Trane Chiller.

- Replace display adaptive control and cover.

- Check unit operations.