        Fahrenheit Incorporated Mechanical Contracting
        85 Farless Avenue
        Telephone (732) 673- 9318
        E-mail: Celcius60@aol.com

Joe Bayne CMI NY-024 bldg #356

INVOICE------THIS WORK WAS COMPLETED—FEB 7th,2023
  NY-024—Bldg,#356--CSS#-91366--WO#-20601
1/9/23 Job Description
Emergency service call ---office air handler coil split from loss of power causing outside air damper to stay-open with freezing outdoor conditions. Scope of work: Disconnect supply and return lines from air handler heating coil , disconnect freeze stat from existing coil, remove all support brackets securing coil, remove coil from existing air-handler, Braze and repair existing coil could not get new coil to fit this air-handler for 6 weeks recommend repairing existing coil also, I would recommend adding Glycol to entire heating system, This will be an additional proposal with the same CSS# since the time line for getting glycol will be 2-weeks from this approval, also recommend changing actuator on outside air damper and lubricate outside air damper linkages, Re-place circuit setter and all necessary fittings and Y-type strainer to establish all necessary flow through coil.--Materials to include: Brazing type silfos rods,- $221.00- 1-1/2 iron body Y-strainer,-$83.85- 10-ft of 1-1/2 l-tubing,-$136.41- 2-1-1/2” copper unions,-$198.60- 2- 3/4”-boiler drains,-$33.56- 1- roll of 95/5 solder,-$33.74-Re-fill tanks-actylene,oxygen,-$156.50-4-1-1/2”copper slip couplings,-$45.55- 1- roll of emery paper,-$15.10- 1-container of tefylon paste-$58.55- 1-roll of lampwick,-$5.25-2- runs of 1-1/2”-blk nipples,-$99.48--1-run-3/4”blk steel nipples,-$31.33,2-3/4”-Nibco ball valves,-$37.28,-Labor will be 3days 1- mechanic and helper which will discount the emergency service call of $400 ----------$3600-------Total materials with repairing of existing coil ----$1,156.20--Total cost with labor and materials-----------$4756.20 THIS PROPOSAL WILL NOT INCLUDE ACTUATOR OR ANY GLYCOL THIS PRICE WILL ONLY FOR GETTING SYSTEM BACK UP AND RUNNING TO PROVIDE HEATING FOR THESE OFFICES: