        Fahrenheit Incorporated Mechanical Contracting
        85 Farless Avenue
        Telephone (732) 673- 9318
        E-mail: Celcius60@aol.com

CMI—Joe Bain Bldg #208 fort wadsworth S.I.

CSS # 34774 Job Description
After troubleshooting Triad condensing type boiler located in basement mechanical room bldg #208 found hi limit safety control not operating at proper shut-off temperture must replace control also clean combustion screen and set parameters on honeywell control module.---Materials required; 1—factory hi limit safety control –part #262-0000077-----$368.92. Labor to include, Draining down boiler installing new control cleaning burner screen re-filling system and purging all air out. 1-mechanic and helper 10hrs total which includes all travel expenses and tolls.---$1,500.---------------Total cost------$1,868.92